|  |  | Substation |  |  | HABU HEIGHT |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  |  |  | Time: 5:38 PM |  |  |  |  |
|  |  | Model |  |  |  |  | Rating |  |  |  |  |  |  |  |  |  |  | Humidity: 77% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW TOP |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 2 |  |  |  |  |
| Location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 29.9 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 30.2 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  |  |  |  |  |  |
|  | Average Temp. (Ar1) |  | 30.0 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 20.9 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.4 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Defect |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis & Recommendations:

Analysis: No Anomaly.

Recommendation: -