|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | INDKOM |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | INS24 |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW |  |  |  |  |  |  |  |  |  |  | Panel No. |  | - |  |  |  |  |
| Panel Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 18072222340DE |  |  |  |  |
|  | Average Temp. (Ar1) |  | 24.2 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | INDKOM |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | INS24 |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW TOP |  |  |  |  |  |  |  |  |  |  | Panel No. |  | - |  |  |  |  |
| Panel Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 18072222340DE |  |  |  |  |
|  | Average Temp. (Ar1) |  | 23.7 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | INDKOM |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | INS24 |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00420 |  |  |  |  |
| Panel Name |  | BERTAM MEWAH |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 24.0 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 23.9 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 18072222340DE |  |  |  |  |
|  | Average Temp. (Ar1) |  | 24.1 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.1 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | NOT ACCESSIBLE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | INDKOM |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | INS24 |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00423 |  |  |  |  |
| Panel Name |  | CS JENSIN |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 23.7 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 23.7 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 18072222340DE |  |  |  |  |
|  | Average Temp. (Ar1) |  | 23.9 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.0 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | NOT ACCESSIBLE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | INDKOM |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | INS24 |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00422 |  |  |  |  |
| Panel Name |  | OUF |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 23.7 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 23.8 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 18072222340DE |  |  |  |  |
|  | Average Temp. (Ar1) |  | 23.9 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.0 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | NOT ACCESSIBLE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | INDKOM |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | INS24 |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00421 |  |  |  |  |
| Panel Name |  | TX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 24.2 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 24.3 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 18072222340DE |  |  |  |  |
|  | Average Temp. (Ar1) |  | 24.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.1 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | NOT ACCESSIBLE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  | EWT |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | HERMETICALLY SEAL |  | Rating |  |  |  |  |  |  |  |  | 750kVA |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 1 |  |  |  |  |
| Location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 31.7 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 35.7 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | EWT55674 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 34.6 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 4.0 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Defect |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis & Recommendations:

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  | EWT |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | HERMETICALLY SEAL |  | Rating |  |  |  |  |  |  |  |  | 750kVA |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | BUSHING |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 1 |  |  |  |  |
| Location |  | HV SIDE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 26.9 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 28.6 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | EWT55674 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 28.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | -1.6 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | 0dB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | Normal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  | EWT |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | HERMETICALLY SEAL |  | Rating |  |  |  |  |  |  |  |  | 750kVA |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 1 |  |  |  |  |
| Location |  | HV SIDE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 26.5 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 26.1 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | EWT55674 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 28.4 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.5 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | 0dB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | Normal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  | EWT |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | HERMETICALLY SEAL |  | Rating |  |  |  |  |  |  |  |  | 750kVA |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | BUSHING |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 1 |  |  |  |  |
| Location |  | LV SIDE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 25.8 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 28.9 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | EWT55674 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.5 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 3.2 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  | EWT |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | HERMETICALLY SEAL |  | Rating |  |  |  |  |  |  |  |  | 750kVA |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 1 |  |  |  |  |
| Location |  | LV SIDE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 21.5 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 24.8 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | EWT55674 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 23.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 3.3 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | FP TX1 |  | Manufacturer |  |  |  |  |  |  |  |  | PSB |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | DIN TYPE |  | Rating |  |  |  |  |  |  |  |  | 1600A |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW |  |  |  |  |  |  |  |  |  |  | Feeder No. |  | - |  |  |  |  |
| Feeder Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | RTLR 642-045 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 27.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -