|  |  | Substation |  |  | BERTAM VALLEY |  |  |  |  |  |  |  |  |  |  |  |  | Date: 02/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | TRANSFORMER |  | Manufacturer |  |  |  |  |  |  |  |  | EWT |  | Time: 9:20 AM |  |  |  |  |
|  |  | Model |  |  | HERMETICALLY SEAL |  | Rating |  |  |  |  |  |  |  |  | 750kVA |  | Humidity: 79% |  |  |  |  |
|  |  | Area |  |  | CABLE |  |  |  |  |  |  |  |  |  |  | Tx No. |  | 1 |  |  |  |  |
| Location |  | LV SIDE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 21.5 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 24.8 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | EWT55674 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 23.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 3.3 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -