|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW |  |  |  |  |  |  |  |  |  |  | Panel No. |  | - |  |  |  |  |
| Panel Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  |  |  |  |  |  |
|  | Average Temp. (Ar1) |  | 27.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW TOP |  |  |  |  |  |  |  |  |  |  | Panel No. |  | - |  |  |  |  |
| Panel Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  |  |  |  |  |  |
|  | Average Temp. (Ar1) |  | 27.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW BOTTOM |  |  |  |  |  |  |  |  |  |  | Panel No. |  | - |  |  |  |  |
| Panel Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  |  |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.6 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Defect |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Analysis: No Anomaly.

Recommendation: -

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00347 |  |  |  |  |
| Panel Name |  | KTRS TNB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 27.2 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 27.3 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 27.3 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.2 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | CABLE ENTRY |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00347 |  |  |  |  |
| Panel Name |  | KTRS TNB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 26.8 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 27.1 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.9 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.3 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00346 |  |  |  |  |
| Panel Name |  | LOJI AIR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 26.8 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 26.9 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.9 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.1 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | CABLE ENTRY |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00346 |  |  |  |  |
| Panel Name |  | LOJI AIR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 26.0 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 26.1 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.4 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.2 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | CABLE COMPARTMENT |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00345 |  |  |  |  |
| Panel Name |  | SSU HABU |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 27.1 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 26.8 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.6 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.3 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | S/S LOJI AIR HABU |  |  |  |  |  |  |  |  |  |  |  |  | Date: 01/06/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | RMU SF6 |  | Manufacturer |  |  |  |  |  |  |  |  | TAMCO |  | Time: 4:21 PM |  |  |  |  |
|  |  | Model |  |  | FALCON BETA |  | Rating |  |  |  |  |  |  |  |  | 12kV |  | Humidity: 80% |  |  |  |  |
|  |  | Area |  |  | CABLE ENTRY |  |  |  |  |  |  |  |  |  |  | Panel No. |  | CCH00345 |  |  |  |  |
| Panel Name |  | SSU HABU |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 26.7 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 25.8 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 26.2 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 21.2 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | CLOSE |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.8 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Defect |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | (( panel.db_level }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ panel.us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: No Anomaly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |